Fosroc Conbextra GP

Economical, Class A shrinkage compensated grout 
(for gaps 10mm to 100mm thickness)

*1.0

Grouting Requirements

To the nominated area(s) (specify details and areas of application), grouting must be carried out using a pre-packaged, chloride free, dry powder blend of cements, graded fillers and chemical additives.

It is to be mixed with clean water to the required consistency. The plastic grout must not bleed or segregate. The storage, handling and placement of the grout must be in strict accordance with the manufacturer’s instructions.

A positive volumetric expansion of 1-3% shall occur while the grout is plastic by means of a gaseous system.

It shall exhibit Flow Characteristics when tested to AS 1478.2.2005 of 400 – 600mm using the flow trough procedure.

It shall be formulated to exhibit the following characteristics when mixed with 3.2 litres of water to one 20kg bag of the specified grout, at flowable consistency, when tested @ 23oC:

Compressive Strength 	1 day 32MPa

(AS 1478.2.2005) 		7 days 43MPa

28 days 65MPa

Indirect Tensile Strength 	1 day 3.5Mpa

(AS 1010.10 – 2000) 		7 days 5.6MPa

28 days 6.1MPa

Modulus of Rupture 		1 day 4.4MPa

(Flexural Strength) 		7 days 8.7MPa

(AS 1012.11 – 2000) 		28 days 13.6MPa

Fosroc Conbextra GP manufactured by Parchem Construction Supplies meets the performance criteria and is approved for this application.